| MOP HISTORY |  |  |  |  |
| --- | --- | --- | --- | --- |
| MOST RECENT VERSION | REVISION DETAIL/S | AUTHOR | APPROVED BY | DATE APPROVED |
| 1.0 | 1st DRAFT | John Carlo Rabanes |  |  |

1. DESCRIPTION

- Power tapping of Site Nokia OLT CDO-604 System

2. PURPOSE AND SCOPE

PURPOSE - To power on CDO-604(mini OLT) for B2B as a pre-requisite of Site deployment. SCOPE - Nokia Lightspan MF-2 (Mini OLT power tapping of DC +48Vdc breakers/panels. PROPOSED RECTIFIER SYSTEM LOAD BREAKER FUSE: (RECTIFIER 1) FUSE No: {{load}}+ Equipment –(Nokia Power tappingpoint) {{RS1 Load schedule image}} PROPOSED RECTIFIER SYSTEM LOAD BREAKER FUSE: (RECTIFIER 2 ) FUSE No: L6 Nokia OLT MF-2 – ( Nokia Power tapping point) {{RS2 Load schedule image}}

3. BACKGROUND

- This activity will support the Blaine Plus Project for additional OLT GPON/VOICE deployment of Nokia OLT MF-2 equipment for the Globe Project

| 4. PROPONENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name | Position | Dept./Div. | Signature | Date |
| Dhenver Santos | Technical Team Head | Nokia / OLT MF-2 |  |  |
| Edgar Peralta | OLT Supervisor | Nokia / OLT MF-2 |  |  |
| John Carlo Rabanes | OLT Engineer | Nokia / OLT MF-2 |  |  |
| Kristy Mae Dela Torre |  |  |  |  |
| Butch Doble |  |  |  |  |

Note: Required Signatories Minor – up to Section Head Major – up to Department Head Critical – up to Division Head

5. Target Date and Time of Implementation: < May 19- June 19, 2026 10:00AM-6:00PM>

| 6. CHANGE CATEGORY |  |  |
| --- | --- | --- |
| Minor | Major | Critical |

| 7. TYPE OF SERVICES AFFECTED |  |  |
| --- | --- | --- |
| Service : (None Service Affecting) | Product : | MVNO /IR/Others : |

| 8. SITE AND E2E SYSTEM AFFECTED |  |
| --- | --- |
| Site(Location) | System (E2E) |
| CDO-604_MIN995 | OLT MF-2 |

9. E2E SYSTEMS BLOCK DIAGRAM

| 10. WITH OTHER RELATED ACTIVITY: YES NO |  |
| --- | --- |
| Description |  |
| SO REF# |  |
| MOP REF# |  |
| Other Network Element (NE) Affected |  |
| Remarks: |  |

| 11. SPECIFIC NODE AFFECTED IN THIS MOP |  |  |  |
| --- | --- | --- | --- |
| HARDWARE |  |  |  |
| System Name | Product | Version | Remarks |
| N/A | N/A | N/A |  |
| SOFTWARE |  |  |  |
| System Name | Product | Version | Remarks |
| N/A | N/A | N/A |  |

| 12. PEOPLE INVOLVED DURING IMPLEMENTATION OF THE ACTIVITY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Company | Department | Name | Role | Contact Number |
| Nokia | FN Access Project | Edgar Peralta Jr. | Engineer / implementer | +63 9260895345 |
| Nokia | FN Access Project | Jay Palasol | Engineer / implementer | +63 9175520623 |
| Nokia | FN Access Project | Mark Inovero | Engineer / implementer | +63 9354376033 |
| Nokia | FN Access Project | Mark Brillantes | Engineer / implementer | +63 9562570282 |
| Nokia | FN Access Project | John Carlo Rabanes | Engineer / implementer | +63 9669343065 |
| ESCALATION PROCEDURE |  |  |  |  |
| Company | Department | Name | Role | Contact Number |
| Globe |  | Kristy Mae Dela Torre | Engineering |  |
| Globe |  | Edward Ian Oria | Engineering |  |
| Globe | SICE | LA Tan | Implement Engineering | +63 9178382974 |

| 13. INVENTORY |  |  |  |
| --- | --- | --- | --- |
| HARDWARE |  |  |  |
| System Name | Product | Version | Remarks |

| CDO-604 | OLT MF-2 | L6GQFC24.298 |  |
| --- | --- | --- | --- |
| SOFTWARE |  |  |  |
| System Name | Product | Version | Remarks |
| CDO-604 | OLT MF-2 | L6GQFC24.298 |  |

| 14. SUPPORTING DOCUMENTS |  |
| --- | --- |
| Reference Number | Description |
| Approved TSSR / Technical power proposal | Please see attached signed tssr. MIN995_CDO-604 |

| 15. WORK BREAKDOWN SCHEDULE |  |  |  |  |
| --- | --- | --- | --- | --- |
| Start Time | End Time | Activity | Responsible | Remarks |
| 09:00 | 10:15 | Pre-activity procedure | FAPE/ Nokia Engineer |  |
| 10:15 | 12:30 | Activity Proper | Nokia Engineer |  |
| 12:30 | 18:00 | Post-activity procedure | FAPE/ Nokia Engineer |  |

16. KNOWN ISSUES, RISKS AND MITIGATIONS (Preventive)

MITIGATIONS - Insulation testing should be done prior activity - Spare breaker should be available - Power cable route are inspected prior activity RISKS - Power cables & DC Breakers are faulty KNOWN ISSUES - N/A

17. PRE-REQUISITES PRIOR IMPLEMENTATION

SAT / ISAT / IOT Tests : N/A

Permit to Work: Yes RAAWA: Yes HEO/FO Resource Availability/ Test Callers Availability: N/A Vendor Support: Yes No Existing Fault: Yes Availability of Spare Modules, Patch Cords , etc: N/A Section/Dept/Division Head Approval: N/A Business Approval: N/A Baseline stats: N/A

18. SUCCESS, ABORT AND REVERT BACK CRITERIA

SUCCESS CRITERIA - OLT MF-2 is powered-on without interruption. - No alarms are observed during the activity. ABORT CRITERIA - There are existing faults in rectifier or DCDU. REVERT CRITERIA - Unexpected outage occurred on GAIN network caused by the activity. (Please call Proponent first before revert to verify).

19. PRE-ACTIVITY PROCEDURES

- SCC Wireline to check and validate existing alarms on NMS. - Visual inspection of power cables (labels, breakers, rectifier loadings, etc.) - Assistance from Globe proponent/Facilities for checking of rectifier and PDF status.

20. PLANNED ACTIVITY PROCEDURES

1. Aligned the breaker assignment as follows : Fuse L9 (63A) : Nokia Power Tapped Fuse L17 (16A) : Nokia Power Tapped

{{RS1 EXISTING IMAGE}} RECTIFIER 1 {{RS2 EXISTING IMAGE}} RECTIFIER 2 A. Tap the power cables on the PDF breakers with respect to equipment power modules. - Make sure power tapping of the breaker is for the terminals of the equipment. Also the breaker should be switched off prior to the tapping of cable/s. - One by one, tap the cable/s to their respective breakers. Be sure not to cause any short circuit in the cables being tapped or any other cables in the power panel. Make sure that the cable/s is properly terminated to their terminals (with the appropriate terminal lugs) and all terminations are properly tightened. - Apply the corresponding label after the said activity.

20. POST ACTIVITY CHECKING AND VALIDATION

- NOC Wireline to check and validate existing alarms on NMS. - Visual inspection of power cables (labels, breakers, rectifier loadings, etc.) - Assistance from Globe proponent/Facilities for checking of rectifier and PDF status. - Visual inspection of AMS server power LED. - Visual inspection of SWITCH power LED.

21. REVERT BACK PROCEDURES

In case of revert, power off the breakers.

22. POST REVERT BACK SUCCESS CRITERIA

- NOC Wireline to check and validate existing alarms on NMS. - Visual inspection of power cables (labels, breakers, rectifier loadings, etc.) - Assistance from Globe Proponent/Facilities for checking of rectifier and PDF status.

23. CONTINGENCY (If Revert Procedure Fails)

- Contact GT proponent / Nokia proponent (refer to escalation procedure)

24. MOP REVISION DETAILS (to be filled in by SEI reviewing engr)

REVISION 1 : (indicate reason)

Lack of Mandatory Information Configuration not aligned with standard / LLD Confusing instruction in the procedure Missing Configuration Missing step in procedure Wrong Configuration Typing Error Incorrect Data

REVISION 2 : (indicate reason based on same list above)

REVISION 3 : (indicate reason based on same list above)